| Product name | Rechargeable Li-ion Cell (TÜV RH approved) | Rechargeable Li-ion Module | Rechargeable Li-ion Battery System |
| --- | --- | --- | --- |
| Type/model | CB2W0 (Contemporary Amperex Technology Co., Limited, CB by TÜV R) | IBP14K513C(内置), IBP14K514C | IBS215K1KC3 （内置模组）, IBS215K1KC4 系统只有2个型号？还是要出系列？ |
| BMS model | -- | 从控BSU有2部分: Part 1: BSU02S2 (硬件版本A00) for IBP14K513C; BSU02S3Z (硬件版本A01) for IBP14K514C; Part 2: BSU02U1, 硬件版本: A03 软件版本：V1.13 AFE: (Q1, BQ79616) (for BSU02S3) 或 (Q1, DNB1101B) (for BSU02S2) MCU: (U2, APM32E103) | 高压箱型号：IBU280A1K 主控板BMU型号: BMU01U1Z 硬件版本: A03 软件版本号:V100.05 电流保险丝: 350A 总压和分流器AFE: (U26, LTC2949) 主MCU（U1, FS32K146） 辅助MCU (U31, KEAZ128) SPI: U2, LTC6820 继电器驱动开关: Q26, Q27 CAN: U7, MC33FS6503 主正KM1, 主负KM2 |
| Configuration | -- | 16S IP20 | 15S IP55，要提供储能柜的IP55的带有CNAS的测试报告； |
| Nominal voltage | 3.2Vd.c. | 51.2Vd.c. | 768.0V |
| Rated capacity | 280Ah, 896Wh | 280Ah | 280Ah |
| Charging voltage declared by manufacturer 推荐充电电压 | 3.65V | 57.6V or 3.6V/cell | 864V or 3.6V/cell |
| Upper limit charging voltage 上限电压 | 3.65V | 57.6V or 3.6V/cell | 864V or 3.6V/cell |
| Charging current declared by manufacturer 推荐充电电流 | 280A | 140A | 140A |
| Maximum continuous Charging Current 最大持续充电电流 | 280A | 140A | 140A |
| Maximum impulse Charging Current 电芯的最大脉冲充电电流 | 320A (t≤60s) | 210A （10min） | 210A （10min） |
| Discharging current declared by manufacturer | 280A | 140A | 140A |
| Maximum continuous discharging current 最大持续放电电流 | 280A | 140A | 140A |
| Maximum impulse discharging current 电芯的最大脉冲放电电流 | 320A (t≤60s) | 210A （10min） | 210A （10min） |
| Discharge Cut-Off Voltage | 2.5V | 41.6V (2.60V/cell) or any cell reaches 2.6V | 624V or any cell reaches 2.6V |
| Standard Charging temp. range | 0oC~60oC | 0oC~50oC | 0oC~50oC |
| Standard discharging temp. range | -20oC ~ 65oC | -20oC ~ 55oC | 0oC ~ 55oC |
| Standard charging method by manufacturer | Charge at constant current 280A until voltage reaches to 3.65V, then charge at constant voltage 3.65V until current is 14A | Charge at constant current 140A until voltage reaches to 57.6V or any cell reaches to 3.6V. Then Rest 5min. Then charge at constant current 14A until voltage reaches to 57.6V or any cell reaches to 3.6V. | Charge at constant current 140A until voltage reaches to 864V or any cell reaches to 3.6V. Then Rest 5min. Then charge at constant current 14A until voltage reaches to 864V or any cell reaches to 3.6V. |
| Standard discharging method by manufacturer 放电方法 | Discharge at constant current 280A until voltage reaches 2.5V | Discharge at constant current 140A until voltage reaches to 41.6V or 2.6V/cell | Discharge at constant current 140A until voltage reaches 624V or any cell reaches 2.6V. |
| Dimension | (71.7±1)mm * (173.9±1)mm * (204.6±1)mm | For IBP14K513C: (454±2.0)mm * (714±2.0)mm * (230±2.0)mm; IBP14K514C: (521±2.0)mm * (743±2.0)mm * (230±2.0)mm (W*D*H) | WidthⅹDepthⅹHeight: 1200mmⅹ1403mm x 2357mm (With air conditioner) |
| Weight | (5.36±0.3)kg | Max. 115Kg | Max. 2500kg |
| Over-voltage protection for cell and for charging 充电单体过压保护值 | 3.65V | - | (3.63±0.01)V/cell, (3±2)s |
| Over-voltage protection for cell and for charging 充电总压过压保护值 | - | - | (864±2.4)V, (3±2)s (3.6V/cell) |
| Under-voltage protection for cell and for discharge 放电单体欠压保护值 | 2.5V | - | (2.6 ±0.01)V/cell, (3±2)s |
| Under-voltage protection for cell and for discharge 放电总压欠压保护值 | - | - | (624±2.4)V, (3±2)s (2.6V/cell) |
| Over-current protection for charging 充电过流 | 320A (t≤60s) | - | (300±5)A, (3±2)s |
| Over-current protection for discharging 放电过流 | 320A (t≤60s) | - | (300±5)A, (3±2)s |
| 短路保护电流 | - |  | 10KA, 200µs |
| High-temperature protection for charging 充电高温 | 0oC~60oC | - | (55±2)℃, (3±2)s |
| Low-temperature protection for charging 充电低温 | - | - | (0±2)℃, (3±2)s 以电芯的热电偶实测值为准，测试值>/=0oC |
| High-temperature protection for discharging 放电高温 | -20oC ~ 65oC | - | (60+2)oC, (3±2)s |
| Low-temperature protection for discharging 放电低温 | - | - | (-20±2)℃, (3±2)s |
|  |  | Case 1: 4 NTCs Case 2: 16NTCs | Case 1: 15个AFE, 共有60 NTCs Case 2: 16*15=240NTCs |
| 预充功能 | - | - | 预充的继电器触点粘连后，要断总负继电器做第二重保护，从而切断充放电主回路； |
| 电芯是否有加热膜？ |  |  | 加热继电器触点粘连后，要断总负继电器 ---无加热！ |
| 单体压差保护 | - | - | 300mV |
| 单体采样的累加和与采样的系统电压之间的压差保护值 | - | - | 10V |
| 电流差值（分流器与霍尔） | - | - | 15A |
| 电芯NTC之间的温差保护值 | - | - | 30℃ |