| Standard: IEC 60730-1: 2013+A1+A2; |  |  |  |
| --- | --- | --- | --- |
| Client: | INFY POWER | Product: | Rechargeable Li-ion Battery System |
| Test by: |  | Review by: |  |
| Test Date: | 2023-08-08 | Review Date: |  |
| Full-test: |  |  |  |
| Re-test: |  |  |  |

# Fault Insertion Tests

| Result Fail or Pass | Clause(s) | Test(s) |
| --- | --- | --- |
| F P | 3.1 | ## BMS function and Hardware single-fault test |
| F P | 3.2 | Software fault insertion test |

General

The Equipment under Test (EuT) is a battery with BMS built-in. (带着电池做测试！注意安全！)

# Test equipment

## Test equipment Client 测试用设备信息

Attention:

Check that

- the calibration/verification records of test and measuring equipment indicate that calibration is traceable to national/international standards of measurement.

- the records for calibration/verification of test and measuring equipment are maintained and satisfactory.

- the calibration record shall be issued by a CNAS (national) or an ILAC (international) accredited laboratory

请详细列出所用的设备！

| No. | Name设备名称及ID | Identifier设备参数范围 | Calibration校准到期日 |
| --- | --- | --- | --- |

Table 1: Test equipment Client

2Remark: The used equipment has to be identified within the tables of chapter  .

# Test sample(s)

| No. | Name | Serial No./Identifier |
| --- | --- | --- |

Table 2: Test samples

## Test sample HW revision:

| Schematics 硬件板 & Version版本 | Date |
| --- | --- |
| 样品1： BSU02S2 (硬件版本A00)+ BSU02U1 (硬件版本: A03) + BMU01U1Z (A03) 样品2： BSU02S3Z (硬件版本A01) BSU02U1 (硬件版本: A03)+ BMU01U1Z (A03) |  |

Table 3: HW revision

## Test sample SW revision

| Firm-/Software 软件版 & Version版本 | Date |
| --- | --- |
| BSU: V1.13 + BMU: V100.05 |  |

Table 4: SW revision

## Definition of the safe state

| Test sample | Safe State |
| --- | --- |
| /S1/ | Safety state: relat off (1st) or relay off (2nd) Safety functions: 1.电芯单体电压保护功能: 用于保证电芯电芯电压工作在安全范围内; 2.电芯电流保护功能: 用于保证电芯电流工作在安全范围内; 3.电芯温度保护功能:用于保证电芯温度工作在安全范围内 无论是硬件故障，还是软件故障，产品在发现故障后，首先要进入安全状态，就是首先要切断继电器！！！ |

Table 5: Definition Safe State

# Fault insertion testing (FIT)

测试结果要包括：

- 故障在硬件上的搭建和实现，以及对应电路图上的故障点拍照或者视频；

- 样品和测试设备的设置拍照；

- 测试后样品，PACK面板的显示，上位机的截图，PCB板上的故障点的情况；

- 故障去除后，样品能否复位，进行正常的充电放电；

## BMS function and Hardware single-fault test

（下面所有的测试拍视频，BMS动作前后上位机的显示界面，和报警界面信息-显示是什么元件动作断开！）

| ### _ Normal operation - cell overvoltage during charge (用BSU02S2从控板做下面的过压和欠压的单压和总压保护的4个验证测试) 充电单体过压保护和 延迟时间验证 |  |
| --- | --- |
| Safety criteria/Function | Overvoltage protection |
| Component and Failure-mode | Charge the cell until voltage reached overvoltage limit (3.63V, 3s) until BMS operate. 常温下140A充电，直到BMS发生单压过充保护动作 |
| Condition | Run运行检（环温: oC） BMS动作时，记录下面的数据 |
| Test result by practical test | Test 1: Simulate 1 Cell Overvoltage: 可以总体过压或者 选择1颗电芯过充, 分别使用校准设备测量电芯电压和响应时间, 并记录对应的BMS读出的电芯电压 No.; Cell voltage measured by calibrated meter 用万用表测量发生过充保护的电芯的单芯电压; Cell voltage measured by BMS 上位机的读数; Response time ≤5s （延迟时间的测量可以通过示波器抓取单芯电压达到3.63V与BMS动作之间的时间差，也可以通过读取BMS上位机的报文；）. 1. 哪个继电器动作？. Test 2: Above relay short-circuit, then simulate 1 cell overcharge: 模拟主正relay失效, 继续充电, 验证第二重保护 – 总负relay是否动作. 2; --. Negative relay operated or not？总负relay是否动作 (Yes / No). |
| Comments | Test 1: NA F P Test 2: NA F P |
| 测试用设备： |  |

| ### _ Normal operation - cell undervoltage during discharge (BSU02S2) 放电单体欠压保护和 response time验证 |  |
| --- | --- |
| Safety criteria/Function | Undervoltage protection |
| Component and Failure-mode | Discharge the cell until voltage reached undervoltage limit (2.6V, 3s) until BMS operate. 140A放电，直到单压欠压保护BMS动作 |
| Condition | Run运行检（环温: oC） BMS动作时，记录下面的 |
| Test result by practical test | Test 1: Simulate 1 Cell undervoltage: 总体放电或者选择1颗电芯做到过放保护, 分别使用校准设备测量电芯电压和响应时间, 并记录对应的BMS读出的电芯电压 No.; Cell voltage measured by calibrated meter 用万用表测量过充电芯的单芯电压; Cell voltage measured by BMS 上位机的读数; Response time ≤5s. 1. 哪个继电器动作？. Test 2: Above relay short-circuit, then simulate 1 cell overcharge: 模拟主负relay失效, 继续充电, 验证第二重保护 – 主正relay是否动作. 2; --. Positive relay operated or not？主正relay是否动作 (Yes / No). |
| Comments | Test 1: NA F P Test 2: NA F P |

| ### _ Normal operation - cell overvoltage during charge 充电总体过压保护和 延迟时间验证 （首先失效单压保护！选择BSU02S2测试） |  |
| --- | --- |
| Safety criteria/Function | Overvoltage protection |
| Component and Failure-mode | Charge the cell until voltage reached overvoltage limit (864V, 3s) until BMS operate. 常温下140A充电，直到BMS发生总压过充动作 |
| Condition | Run运行检（环温: oC） BMS动作时，记录下面的数据 |
| Test result by practical test | No.; Cell voltage measured by calibrated meter 用万用表测量系统总压 （保护动作前的最大电压！）; Cell voltage measured by BMS 上位机的总压读数; Response time ≤5s （延迟时间的测量可以通过示波器，也可以通过读取BMS上位机的报文；）. 1. 哪个继电器动作？. |
| Comments | Test 1: NA F P |

| ### _ Normal operation - cell undervoltage during discharge (BSU02S2) 放电总压欠压保护和 response time验证 |  |
| --- | --- |
| Safety criteria/Function | Undervoltage protection |
| Component and Failure-mode | Discharge the cell until voltage reached undervoltage limit (624V, 3s ) until BMS operate. 140A放电，直到总压欠压保护BMS动作 |
| Condition | Run运行检（环温: oC） BMS动作时，记录下面的 |
| Test result by practical test | No.; Cell voltage measured by calibrated meter 用万用表测量电池系统总压（保护动作前的最大电压！）; Cell voltage measured by BMS 上位机的总压读数; Response time ≤5s. 1. 哪个继电器动作？. |
| Comments | Test 1: NA F P |

| ### _ Normal operation - cell overvoltage during charge (用样品2 --BSU02S3Z从控板做下面的过压和欠压的单压和总压保护的4个验证测试) 充电单体过压保护和 延迟时间验证 |  |
| --- | --- |
| Safety criteria/Function | Overvoltage protection |
| Component and Failure-mode | Charge the cell until voltage reached overvoltage limit (3.63V, 3s) until BMS operate. 常温下140A充电，直到BMS发生单压过充保护动作 |
| Condition | Run运行检（环温: oC） BMS动作时，记录下面的数据 |
| Test result by practical test | Test 1: Simulate 1 Cell Overvoltage: 可以总体过压或者 选择1颗电芯过充, 分别使用校准设备测量电芯电压和响应时间, 并记录对应的BMS读出的电芯电压 No.; Cell voltage measured by calibrated meter 用万用表测量发生过充保护的电芯的单芯电压; Cell voltage measured by BMS 上位机的读数; Response time ≤5s （延迟时间的测量可以通过示波器，也可以通过读取BMS上位机的报文；）. 1. 哪个继电器动作？. Test 2: Above relay short-circuit, then simulate 1 cell overcharge: 模拟主正relay失效, 继续充电, 验证第二重保护 – 总负relay是否动作. 2; --. Negative relay operated or not？总负relay是否动作 (Yes / No). |
| Comments | Test 1: NA F P Test 2: NA F P |
| 测试用设备： |  |

| ### _ Normal operation - cell undervoltage during discharge (BSU02S3Z) 放电单体欠压保护和 response time验证 |  |
| --- | --- |
| Safety criteria/Function | Undervoltage protection |
| Component and Failure-mode | Discharge the cell until voltage reached undervoltage limit (2.6V, 3s ) until BMS operate. 140A放电，直到单压欠压保护BMS动作 |
| Condition | Run运行检（环温: oC） BMS动作时，记录下面的 |
| Test result by practical test | Test 1: Simulate 1 Cell undervoltage: 总体放电或者选择1颗电芯做到过放保护, 分别使用校准设备测量电芯电压和响应时间, 并记录对应的BMS读出的电芯电压 No.; Cell voltage measured by calibrated meter 用万用表测量过充电芯的单芯电压; Cell voltage measured by BMS 上位机的读数; Response time ≤5s. 1. 哪个继电器动作？. Test 2: Above relay short-circuit, then simulate 1 cell overcharge: 模拟主负relay失效, 继续充电, 验证第二重保护 – 主正relay是否动作. 2; --. Positive relay operated or not？主正relay是否动作 (Yes / No). |
| Comments | Test 1: NA F P Test 2: NA F P |

| ### _ Normal operation - cell overvoltage during charge 充电总体过压保护和 延迟时间验证 （首先失效单压保护！选择BSU02S3Z测试） |  |
| --- | --- |
| Safety criteria/Function | Overvoltage protection |
| Component and Failure-mode | Charge the cell until voltage reached overvoltage limit (864V, 3s) until BMS operate. 常温下140A充电，直到BMS发生总压过充动作 |
| Condition | Run运行检（环温: oC） BMS动作时，记录下面的数据 |
| Test result by practical test | No.; Cell voltage measured by calibrated meter 用万用表测量系统总压 （保护动作前的最大电压！）; Cell voltage measured by BMS 上位机的总压读数; Response time ≤5s （延迟时间的测量可以通过示波器，也可以通过读取BMS上位机的报文；）. 1. 哪个继电器动作？. |
| Comments | Test 1: NA F P |

| ### _ Normal operation - cell undervoltage during discharge (BSU02S3Z) 放电总压欠压保护和 response time验证 |  |
| --- | --- |
| Safety criteria/Function | Undervoltage protection |
| Component and Failure-mode | Discharge the cell until voltage reached undervoltage limit (624V, 3s) until BMS operate. 140A放电，直到总压欠压保护BMS动作 |
| Condition | Run运行检（环温: oC） BMS动作时，记录下面的 |
| Test result by practical test | No.; Cell voltage measured by calibrated meter 用万用表测量电池系统总压（保护动作前的最大电压！）; Cell voltage measured by BMS 上位机的总压读数; Response time ≤5s. 1. 哪个继电器动作？. |
| Comments | Test 1: NA F P |

| ### _ Normal operation - overcurrent during charge 充电过流保护和 response time验证 |  |
| --- | --- |
| Safety criteria/Function | Overcurrent protection |
| Component and Failure-mode | Charge the battery with overcurrent (300A, 3s) until BMS operate. |
| Condition | Run运行检（环温: oC） BMS动作时，记录下面的 |
| Test result by practical test | Test 1: Simulate Cell overcurrent: 300A充电 给电池包过流充电, 分别使用校准设备测量电流和响应时间, 并记录对应的BMS读出的电流 No.; Current measured by calibrated meter 用万用表测量的电路的电流; Current measured by BMS 上位机的电流读数; Response time ≤5s (延迟时间的测量可以通过示波器抓取电流到300A与BMS动作之间的时间差，也可以通过读取BMS上位机的报文). 1. 哪个继电器动作？. Test 2: Above relay short-circuit, then simulate 1 cell overcharge: 模拟上面的主正relay失效, 继续充电, 验证第二重保护 – 总负relay是否动作. 2; --. Negative relay operated or not？总负relay是否动作 (Yes / No). |
| Comments | Test 1: NA F P Test 2: NA F P |

| ### _ Normal operation - overcurrent during discharge 放电过流保护和 response time验证 |  |
| --- | --- |
| Safety criteria/Function | Overcurrent protection |
| Component and Failure-mode | Discharge the battery with overcurrent (300A, 3S) until BMS operate. 300A放电 |
| Condition | Run运行检（环温: oC） BMS动作时，记录下面的 |
| Test result by practical test | Test 1: Simulate Cell overcurrent: 给电池包过流放电, 分别使用校准设备测量电流和响应时间, 并记录对应的BMS读出的电流 No.; Current measured by calibrated meter 用万用表测量的电路的电流; Current measured by BMS 上位机的电流读数; Response time ≤5s. 1. 哪个继电器动作？. Test 2: Above relay short-circuit, then simulate 1 cell overcharge: 模拟主负relay失效, 继续充电, 验证第二重保护 – 主正relay是否动作. 2; --. Positive relay operated or not？主正relay是否动作 (Yes / No). |
| Comments | Test 1: NA F P Test 2: NA F P |

| ### _ Normal operation – Cell over temperature during charge (用样品1 -- BSU02S2从控板做下面的充电和放电的高温和低温保护的4个验证测试) ### 充电高温保护和 response time验证 ### (验证BMS动作时电芯上的热电偶测温不能超过电芯的正常参数范围) |  |
| --- | --- |
| Safety criteria/Function | Overtemperature protection |
| Component and Failure-mode | charge the battery at over temperature limit (55°C, response time 3s) during charge until BMS operate. 60度环境箱高温下，电池140A充电直到发生过温保护 |
| Condition | Run运行检（环境箱环温: oC） BMS动作时，记录下面的 |
| Test result by practical test | Test 1: Simulate Cell Overtemperature: 触发电芯高温保护, 分别使用校准设备测量电芯温度和响应时间, 并记录对应的BMS读出的电芯温度 No.; Cell temperature measured by calibrated meter （在最热的电芯上贴热电偶）; Cell temperature measured by BMS 上位机的温度读数; Response time ≤5s. 1. 哪个继电器动作？. Test 2: Above relay short-circuit, then simulate 1 cell overcharge: 模拟上面的relay失效, 继续充电, 验证第二重保护 – 总负relay是否动作. 2; --. Negative relay operated or not？总负relay是否动作 (Yes / No). |
| Comments | Test 1: NA F P Test 2: NA F P |
| 测试所用设备： |  |

| ### _ Normal operation – Cell under temperature during charge (BSU02S2) 充电低温保护和 response time验证 |  |
| --- | --- |
| Safety criteria/Function | Under-temperature protection |
| Component and Failure-mode | Decrease all NTC to under temperature limit (0°C, response time 3s) during charge until BMS operate at 25A. -5度低温下140A充电 |
| Condition | Run运行检（环温: oC） BMS动作时，记录下面的 |
| Test result by practical test | Test 1: Simulate Cell under-temperature: 触发电芯低温保护, 分别使用校准设备测量电芯温度和响应时间, 并记录对应的BMS读出的电芯温度 No.; Cell temperature measured by calibrated meter 电芯上热电偶靠近NTC实测温度; Cell temperature measured by BMS 上位机的温度读数; Response time ≤5s. 1. 哪个继电器动作？. |
| Comments | Test 1: NA F P |

| ### _ Normal operation – Cell over temperature during discharge (BSU02S2) 放电高温保护和 response time验证 |  |
| --- | --- |
| Safety criteria/Function | Overtemperature protection |
| Component and Failure-mode | Heat up all NTC to over temperature limit (60°C, response time 3s) during discharge until BMS operate. 65度高温环境箱中， 140A放电 |
| Condition | Run运行检（环温: oC） BMS动作时，记录下面的 |
| Test result by practical test | Test 1: Simulate Cell Overtemperature: 触发电芯高温保护, 分别使用校准设备测量电芯温度和响应时间, 并记录对应的BMS读出的电芯温度 No.; Cell temperature measured by calibrated meter 电芯上热电偶的实测温度; Cell temperature measured by BMS 上位机的温度读数; Response time ≤5s. 1. 哪个继电器动作？. Test 2: Above relay short-circuit, then simulate 1 cell overcharge: 模拟上面的relay失效, 继续充电, 验证第二重保护 – 总正relay是否动作. 2; --. Positive relay operated or not？主正relay是否动作 (Yes / No). |
| Comments | Test 1: NA F P Test 2: NA F P |

| ### _ Normal operation – Cell under temperature during discharge (BSU02S2) 放电低温保护和 response time验证 |  |
| --- | --- |
| Safety criteria/Function | Under-temperature protection |
| Component and Failure-mode | Decrease all NTC to under temperature limit (-20°C, response time 3s) during discharge until BMS operate. -25度低温 140A放电 |
| Condition | Run运行检（环温: oC） BMS动作时，记录下面的 |
| Test result by practical test | Test 1: Simulate Cell undertemperature: 触发电芯低温保护, 分别使用校准设备测量电芯温度和响应时间, 并记录对应的BMS读出的电芯温度 No.; Cell temperature measured by calibrated meter 电芯上热电偶的实测温度; Cell temperature measured by BMS 上位机的温度读数; Response time ≤5s. 1. 哪个继电器动作？. |
| Comments | Test 1: NA F P |

| ### _ Normal operation – Cell over temperature during charge (用样品2 -- BSU02S3Z从控板做下面的充电和放电的高温和低温保护的4个验证测试) ### 充电高温保护和 response time验证 ### (验证BMS动作时电芯上的热电偶测温不能超过电芯的正常参数范围) |  |
| --- | --- |
| Safety criteria/Function | Overtemperature protection |
| Component and Failure-mode | charge the battery at over temperature limit (55°C, response time 3s) during charge until BMS operate. 60度环境箱高温下，电池140A充电直到发生过温保护 |
| Condition | Run运行检（环境箱环温: oC） BMS动作时，记录下面的 |
| Test result by practical test | Test 1: Simulate Cell Overtemperature: 触发电芯高温保护, 分别使用校准设备测量电芯温度和响应时间, 并记录对应的BMS读出的电芯温度 No.; Cell temperature measured by calibrated meter （在最热的电芯上贴热电偶）; Cell temperature measured by BMS 上位机的温度读数; Response time ≤5s. 1. 哪个继电器动作？. Test 2: Above relay short-circuit, then simulate 1 cell overcharge: 模拟上面的relay失效, 继续充电, 验证第二重保护 – 总负relay是否动作. 2; --. Negative relay operated or not？总负relay是否动作 (Yes / No). |
| Comments | Test 1: NA F P Test 2: NA F P |
| 测试所用设备： |  |

| ### _ Normal operation – Cell under temperature during charge (BSU02S3Z) 充电低温保护和 response time验证 |  |
| --- | --- |
| Safety criteria/Function | Under-temperature protection |
| Component and Failure-mode | Decrease all NTC to under temperature limit (0°C, response time 3s) during charge until BMS operate at 25A. -5度低温下140A充电 |
| Condition | Run运行检（环温: oC） BMS动作时，记录下面的 |
| Test result by practical test | Test 1: Simulate Cell under-temperature: 触发电芯低温保护, 分别使用校准设备测量电芯温度和响应时间, 并记录对应的BMS读出的电芯温度 No.; Cell temperature measured by calibrated meter 电芯上热电偶靠近NTC实测温度; Cell temperature measured by BMS 上位机的温度读数; Response time ≤5s. 1. 哪个继电器动作？. |
| Comments | Test 1: NA F P |

| ### _ Normal operation – Cell over temperature during discharge (BSU02S3Z) 放电高温保护和 response time验证 |  |
| --- | --- |
| Safety criteria/Function | Overtemperature protection |
| Component and Failure-mode | Heat up all NTC to over temperature limit (60°C, response time 3s) during discharge until BMS operate. 65度高温环境箱中， 140A放电 |
| Condition | Run运行检（环温: oC） BMS动作时，记录下面的 |
| Test result by practical test | Test 1: Simulate Cell Overtemperature: 触发电芯高温保护, 分别使用校准设备测量电芯温度和响应时间, 并记录对应的BMS读出的电芯温度 No.; Cell temperature measured by calibrated meter 电芯上热电偶的实测温度; Cell temperature measured by BMS 上位机的温度读数; Response time ≤5s. 1. 哪个继电器动作？. Test 2: Above relay short-circuit, then simulate 1 cell overcharge: 模拟上面的relay失效, 继续充电, 验证第二重保护 – 总正relay是否动作. 2; --. Positive relay operated or not？主正relay是否动作 (Yes / No). |
| Comments | Test 1: NA F P Test 2: NA F P |

| ### _ Normal operation – Cell under temperature during discharge (BSU02S3Z) 放电低温保护和 response time验证 |  |
| --- | --- |
| Safety criteria/Function | Under-temperature protection |
| Component and Failure-mode | Decrease all NTC to under temperature limit (-20°C, response time 3s) during discharge until BMS operate. -25度低温 140A放电 |
| Condition | Run运行检（环温: oC） BMS动作时，记录下面的 |
| Test result by practical test | Test 1: Simulate Cell undertemperature: 触发电芯低温保护, 分别使用校准设备测量电芯温度和响应时间, 并记录对应的BMS读出的电芯温度 No.; Cell temperature measured by calibrated meter 电芯上热电偶的实测温度; Cell temperature measured by BMS 上位机的温度读数; Response time ≤5s. 1. 哪个继电器动作？. |
| Comments | Test 1: NA F P |

## Software fault insertion test 软件故障插入测试

## (需要提供带有插入的故障代码的截图的报告！)

下面的MCU故障，从控MCU (U2, APM32E103)和主控MCU (U1, FS32K146)要分别做下面要求的测试！

| ### Register test 寄存器数据故障 |  |  |
| --- | --- | --- |
| Purpose of test or theoretical impact | register error, should turn off. |  |
| Component and Failure-mode | Simulate 1 bit error in register (stuck at error) |  |
| Condition | Start (先写入错误代码, 再开始运行程序) | Run (先开始运行程序，再暂定写入错误代码，再运行程序) |
| Expected reaction/detection |  |  |
| Comments 故障后进入什么状态？ |  |  |
| Test result by practical test | NA F P | NA F P |

| ### Program counter 程序计数器 |  |  |
| --- | --- | --- |
| Purpose of test or theoretical impact | If program counter wrong, should turn off. |  |
| Component and Failure-mode | Simulate a counter error – stuck at |  |
| Condition | Start | Run |
| Expected reaction/detection |  |  |
| Comments 故障后进入什么状态？ |  |  |
| Test result by practical test | NA F P | NA F P |

| ### Interrupt handling and execution 中断处理和执行 |  |  |
| --- | --- | --- |
| Purpose of test or theoretical impact | If Interrupt handling and execution wrong, should turn off. |  |
| Component and Failure-mode | Simulate a counter error – No interrupt and too frequency 没有中断或者中断太频繁 |  |
| Condition | Start | Run |
| Expected reaction/detection |  |  |
| Comments 故障后进入什么状态？ |  |  |
| Test result by practical test | NA F P | NA F P |

| ### Clock |  |  |
| --- | --- | --- |
| Purpose of test or theoretical impact | If clock wrong, should turn off. |  |
| Component and Failure-mode | Test 1: Simulate a clock error – Wrong frequency 时钟 Test 2: Crystal oscillator stop (晶振停止) Test 3: Crystal oscillator half value (晶振半频) Test 4: Crystal oscillator double value (晶振倍频) |  |
| Condition | Start | Run |
| Expected reaction/detection |  |  |
| Comments 故障后进入什么状态？ |  |  |
| Test result by practical test | NA F P | NA F P |

| ### Invariable memory不可变存储器 |  |  |
| --- | --- | --- |
| Purpose of test or theoretical impact | If Invariable memory wrong, should turn off. |  |
| Component and Failure-mode | Simulate Invariable memory error – single bit faults |  |
| Condition | Start | Run |
| Expected reaction/detection |  |  |
| Comments 故障后进入什么状态？ |  |  |
| Test result by practical test | NA F P | NA F P |

| ### Variable memory可变存储器 |  |  |
| --- | --- | --- |
| Purpose of test or theoretical impact | If Variable memory wrong, should turn off. |  |
| Component and Failure-mode | Simulate Variable memory error – DC fault |  |
| Condition | Start | Run |
| Expected reaction/detection |  |  |
| Comments 故障后进入什么状态？ |  |  |
| Test result by practical test | NA F P | NA F P |

| ### Addressing 存储器寻址 |  |  |
| --- | --- | --- |
| Purpose of test or theoretical impact | If Addressing wrong, should turn off. |  |
| Component and Failure-mode | Simulate Addressing error – stuck at |  |
| Condition | Start | Run |
| Expected reaction/detection |  |  |
| Comments 故障后进入什么状态？ |  |  |
| Test result by practical test | NA F P | NA F P |

| ### Internal data path 内部数据通路 |  |  |
| --- | --- | --- |
| Purpose of test or theoretical impact | If Internal data path--data wrong, should turn off. |  |
| Component and Failure-mode | Simulate Internal data path error – stuck at 数据出错 |  |
| Condition | Start | Run |
| Expected reaction/detection |  |  |
| Comments 故障后进入什么状态？ |  |  |
| Test result by practical test | NA F P | NA F P |

| ### Internal data path 内部数据通路 |  |  |
| --- | --- | --- |
| Purpose of test or theoretical impact | If Internal data path –addressing wrong, should turn off. |  |
| Component and Failure-mode | Simulate Internal data path –addressing – wrong address 地址错误 |  |
| Condition | Start | Run |
| Expected reaction/detection |  |  |
| Comments 故障后进入什么状态？ |  |  |
| Test result by practical test | NA F P | NA F P |

| ### External communication 外部通讯 |  |  |
| --- | --- | --- |
| Purpose of test or theoretical impact | If External communication wrong, should turn off. |  |
| Component and Failure-mode | Simulate External communication error – - Hamming distance - Wrong address 错误的地址 - Wrong point in time错误的时间指针 - Wrong sequence错误频率 |  |
| Condition | Start | Run |
| Expected reaction/detection |  |  |
| Comments 故障后进入什么状态？ |  |  |
| Test result by practical test | NA F P | NA F P |

| ### Digital I/O |  |  |
| --- | --- | --- |
| Purpose of test or theoretical impact | If digital I/O wrong, should turn off. |  |
| Component and Failure-mode | Simulate digital I/O error – 数字I/O 故障 |  |
| Condition | Start | Run |
| Expected reaction/detection |  |  |
| Comments 故障后进入什么状态？ |  |  |
| Test result by practical test | NA F P | NA F P |

| ### A/D and D/A converter |  |  |
| --- | --- | --- |
| Purpose of test or theoretical impact | If A/D and D/A converter wrong, should turn off. |  |
| Component and Failure-mode | Simulate A/D and D/A converter error – A/D转换故障 |  |
| Condition | Start | Run |
| Expected reaction/detection |  |  |
| Comments 故障后进入什么状态？ |  |  |
| Test result by practical test | NA F P | NA F P |

| ### _ simulate the communication error |  |  |
| --- | --- | --- |
| Purpose of test or theoretical impact | simulate the communication error 通讯错误 |  |
| Component and Failure-mode | - Repetition of a message: send the same message in cyclic way 信息重复 - Deletion of data in message: send several messages in cyclic way, delete a byte in one of message. 信息有漏或者删除 - Insertion of data in message: send several messages in cyclic way, add a byte in one of message. 信息增加 - Changed sequence of data in message: send several messages in cyclic way, change sequence number in one of message. 传输顺序有误 - Corrupted data in message: send several messages in cyclic way, change one bit in one of message. 数据损坏 - Delay in sending /receiving the message: do not send required message to host(BMU MCU). 数据延迟 - Masquerade: N/A |  |
| Condition | Start | Run |
| Expected reaction/detection |  |  |
| Comments 故障后进入什么状态？ |  |  |
| Test result by practical test | NA F P |  |